## Sheet1
S/N | FREQUENCY | MAINTENANCE ITEMS | STEPS | EQUIPMENTS | PMNO
1 | Daily | Control Panel | 1. Carry out visual panel inspection 2.Press and hold the Lamp test button in order to test all of the LED lights and the display screen. Note the LED lights and the display screen should remain on until the button is released. | Generator | 1
2 | 4 | Inspection of Engine Air Cleaner | Observe the service indicator for debris. | Instrument Air Compressor A&B | 2
3 | Weekly | Cleaning of Engine Air Cleaner | Clean the air cleaner element or replace the air cleaner element when the air restriction reaches 6 kPa (25 inches of H2O) from the indication on the service indicator. | Instrument Air Compressor A&B | 3
4 | Monthly | Draining of Fuel tank | 1.Check the fuel level 2. Open the drain valve on the bottom of the fuel tank in order to drain any water from the tank | Generator | 4